## MIN REQS
Shelby County Government
RFP 21-006-45, Chiller Maintenance Services Shelby County Government Various Buildings
Department: Support Services
VENDOR: Company name
MINIMUM REQUIREMENTS - 100% on each, to be responsive |  |  |  | VENDOR TO COMPLETE YELLOW SECTIONS
# | Category | Topic | Requirement Description | YES / NO (any "NO" will disqualify you) | Vendor Comments | Ref. to appendix, if applicable
1 | Min req. | License | Provide all appropriate Licenses and Certifications required in the State of Tennessee to provide the goods and/or perform the Services required. Provide a copy of your Shelby County Business License (if business is located in Shelby County, TN).
2 | Min req. | EOC # | Must provide active Equal Opportunity Compliance (EOC) number(s) and Vendor number, or your applications are “in” the EOC system and the Purchasing system for processing (refer to details outlined below) – please list all your Shelby County EOC active numbers.
3 | Min req. | Title VI | Adherence to all provisions of Title VI requirements – please attest, and provide proof/documentation if necessary.
4 | Min req. | Tennessee Lawful Employment Act | Independent Vendors (sole proprietors) must adhere to State of Tennessee Public Chapter No. 436, known as the “Tennessee Lawful Employment Act” (effective date of 01/01/12) – please provide proof and documentation of employment eligibility (driver’s license,…); Otherwise mention you are NOT an Independent Vendors (sole proprietors).
5 | Min req. | LOSB | EOC Compliance FORM A must be completed with active Shelby County Government LOSB vendors listed, signed and included with your proposal, as detailed in this document. FORM B to be completed/signed, with applicable backup, only IF the goal is not met on Form A.
6 | Min req. | Drug Free Workplace | FORM - Drug Free Workplace Affidavit must be completed, signed and notarized with your bid/proposal – even if less than 5 employees.
7 | Min req. | Experience | Must attest to a Minimum of five ( 5 ) years of experience providing the goods and/or performing the services described in this bid.

## DEPT REQS
Shelby County Government
RFP 21-006-45, Chiller Maintenance Services Shelby County Government Various Buildings
Department: Support Services
VENDOR: Company name
DEPARTMENT/SPECIFIC/TECHNICAL REQUIREMENTS |  |  |  |  | VENDOR TO COMPLETE YELLOW SECTIONS
# | Category | Topic | Requirement Description | MAX POINTS | YES-included std FUTURE-not incl. CUSTOM-not incl. NO-not available | Vendor Comments (if custom, add approx. price) | Ref. to appendix, if applicable
1 | Specific Requirements | Maintenance and Repair | The Contractor shall provide all materials (including refrigerant), supplies, supervision, technical and engineering assistance expertise, and subcontracted services necessary to maintain all covered equipment in original factory operating specification condition, consistent with manufacturer’s service recommendations. This includes repair of any failure of any magnitude, using OEM procedures and guidelines, OEM parts, and OEM recommended oils, gaskets, supplies etc. All call out, overtime, travel, and holiday work as needed are included and are not billable as extra. OEM parts are to be used except when they are not available and they are replaced with parts approved as equal by an authorized representative of the Support Services. | 10
2 | Specific Requirements | Equipment Components Covered | In general, this contract covers the chiller controls and all components associated with the refrigerant side of the chiller as well as the refrigerant charge. Coverage includes, as applicable, the control panel, control wiring and tubing, sensors for safeties, compressor and compressor drive train, including electric motor, associated VFD or starter, refrigerant metering and flow control components, all refrigerant sealing devices, refrigerant purge unit, all refrigerant pump out components and building chiller plant refrigerant monitor. The computers, servers, keyboards, printers, monitors and all the chiller controls, valves, relays, etc. that are controlled by the chiller computer are included in this contract. | 10
3 | Specific Requirements | Subcontracts | The Contractor shall be capable of providing the services described within this agreement. The only services that are intended to be subcontracted are such as machining, testing, analysis, or other specialized services. No subcontract work shall relieve the Contractor of its obligation and liability under this contract with the County. | 10
4 | Specific Requirements | Emergency Contact and Response | As a minimum, the Contractor shall provide the County with two (2) contacts and contact methods. A Service Technician must respond to trouble calls within one (1) hour during normal business hours Monday-Friday 8 AM to 5 PM, excluding weekends and County holidays, and two (2) hours outside of normal business hours. Responding to trouble calls means actually commencing appropriate corrective action. | 5
5 | Specific Requirements | Work Outside Scope of Service Contract | Chiller and starter overhaul based on number of operating hours, number of starts or similar measures that establish scheduled tear down and rebuild are outside the scope of this agreement. If scheduled major maintenance is required the Contractor shall provide the County in writing with a composite price including labor, parts, material, and related expenses for these repairs. The County has the option to accept and issue a change order to this agreement implementing such repairs. However, the County retains the option to procure prices from others if deemed necessary. Should alterations, additions, adjustments, or repairs be made by others to any part of the system(s) covered by this service agreement, the Contractor has the right to inspect such work as to having been performed in an acceptable manner to the Contractor prior to continuing the service agreement coverage. The Contractor will notify the County in writing of such conditions, which must be corrected prior to the Contractor acceptance. The Contractor will not be held responsible for damage due to acts of God, freezing, corrosion or erosion due to improper chemical treatment, improper operation by the Owner, fire, water, labor disputes or other incidents that are beyond the control of the Contractor. | 5
6 | Specific Requirements | Parts Stock | The parts stock for all equipment covered herein shall be based on the equipment manufacturer’s recommendations for: routine expendable parts, normal yearly replacement parts, and multi-year replacement parts. The Contractor has the option of stocking locally or by having access to immediate delivery of the parts for the purpose of providing unscheduled service parts on an emergency basis. In either case, the Contractor is expected to have emergency parts available to the County in a reasonable length of time (24 hours) to minimize equipment down time. | 10
7 | Specific Requirements | Waste Oil Disposal | Disposal of all waste oil will be the responsibility of the Contractor. Waste oil will constitute any oil removal from any piece of equipment that is a part of this agreement. All oil removed from serviced equipment will be classified as waste oil and is to be disposed of within the guidelines of EPA regulations. This includes all reports and manifests associated with tracking the waste oil to its final deposition. The Contractor shall provide copies of disposal certification to all required governmental organizations, as well as Shelby County Government Health Department, and the Support Services designee. | 5
8 | Specific Requirements | Compliance with Refrigerant Handling Regulation | Contractor shall fully comply with all current regulations that pertain to refrigerant handling and use. Contractor shall also be responsible for completing and submitting all forms required by State and Federal regulations. The Contractor shall provide copies of disposal certification to the Shelby County Government Health Department, and the Support Services designee. | 5
9 | Specific Requirements | Service Records | The Contractor shall maintain a record of all maintenance and repairs relating to the equipment included in this agreement. At least one copy of all service records will be maintained in a central location; a copy of all service records will be submitted to the County on request. Service reports shall contain the following as a minimum. • Date of Report; • Time period covered by report; • Model and serial number of the inspected/repaired equipment; • Building that the equipment is located in; • Date that service was performed; • A description of the work performed; • Name of technician who performed the work; • Hours charged; • For preventive maintenance, a checklist of activities performed; • Space on the service report will be provided for the Contractor to add appropriate comments, suggestions, or discussions related to the service visit. The Contractor shall provide summaries of all work performed upon completion of the work. The report shall contain: • Date of report; • Date of service; • Brief description of service; • Technician performing work; • Hours Charged; • Provide any additional information to document and alert the County to unusual conditions found, exceptional or unexpected repairs made, suggestions and recommendations to the County, and any pertinent discussion the Contractor determines is worthy of discussion. This report shall include all service reports, be by equipment and formatted to allow compiling history (e.g. separate page for each piece of equipment). The County may request other regular or special reports to allow expeditious retrieval of service information; service records must be maintained in a computerized data base that is Microsoft compatible. | 5
10 | Specific Requirements | Training | The Contractor will provide formal/informal training, as necessary, for any new equipment installation. | 5
11 | Specific Requirements | Schedule of Preventive Maintenance | The Contractor shall submit a proposed schedule of preventive maintenance activities. | 5
12 | Specific Requirements | Outage Procedure | The Contractor shall provide written direction on restarting each plant after a power interruption. | 5
13 | Specific Requirements | Warranty | The chiller and/or its components may be under warranty. However, a warranty does not alleviate the Contractor responsibilities under this contract. The County shall assist in obtaining warranty service or recovery under warranty and shall credit the Contractor the lesser of actual receipts or incurred expenses to the company. | 5
14 | Specific Requirements | Planned Preventive Maintenance | A preventive maintenance program utilizing equipment history, operating hours and equipment manufacturer’s requirements, shall be provided by and supervised by the service company on a scheduled basis. Planned and preventive maintenance shall include the following services as a minimum. Where the manufacturer’s recommendations are more stringent, they shall be followed. A preventive maintenance program utilizing equipment history, operating hours and equipment manufacturer’s requirements, shall be provided by and supervised by the service company on a scheduled basis. Planned and preventive maintenance shall include the following services as a minimum. Where the manufacturer’s recommendations are more stringent, they shall be followed. A. Annual services to be performed during November through March: 1. Control panel test and calibration of the following controls as applicable: a. Low temperature control. b. High pressure control. c. Motor temperature control. d. Oil pressure relief valve setting. e. Check and calibrate load limiting relay. f. Check setting of P.E.’s and calibrate as necessary. g. Check and calibrate temperature controls for leaving chilled water controller h. Set pilot positioner. i. Check gauges for calibration. | 15
2. Oil sump The County may choose to extend the period between oil sump cleanings for specific machines, based on oil sample analysis and other relevant information. The County will only grant such extensions when such extensions are in the County’s own best interest. a. Meg oil pump motor. b. Remove oil sump cover and oil pump and motor assembly. c. Flush oil sump with solvent and thoroughly clean using lint free rags. d. Inspect oil pump assembly for excessive wear. e. Check operation of oil pressure regulator, repair or replace as necessary f. Replace oil strainer cartridges. g. Reassemble oil sump assembly and charge with proper quantity and approved type of oil. h. Provide spectrographic analysis of oil sample. 3. Centrifugal Motor and VFD/Starter a. Clean starter, remove covers for inspection of arc shoots and check spring tension. b. Check all electrical connections for tightness and proper makeup. c. Meg compressor motor. d. Check operation of unit starter/VFD. e. Visually inspect resistors, IGBTs and/or autotransformers; replace as necessary. f. Overloads must be load tested in their own environment. The method of testing overloads shall be by a non-overloading procedure of the motor but using artificial devices on the overloads for a proper test and calibration. g. Vibration test.
4. Leak testing Leak testing shall be performed in accordance with the latest Federal regulations. 5. Oil analysis All oil analyses shall be performed by an individual certified by the service Contractor to be fully qualified to perform such tests. Service Contractor shall also certify that the tests are conducted in accordance with the American Standard Testing Materials Method specifically intended for air condition systems. Test results are to include but not necessarily by limited to the following: a. Machine type and ID number. b. Machine serial number. c. Sample oil number. d. Date of analysis. e. Moisture content in parts per million. f. Total acid content. g. Aluminum in parts per million. h. Chromium in parts per million. i. Copper in parts per million. j. Iron in parts per million. k. Lead in parts per million. l. Tin in parts per million. m. Zinc in parts per million. n. Comments about interpretation of chemical analysis. If an oil analysis report indicates a machine problem, then the service Contractor shall take appropriate action; if an area of concern is identified in the report, the service Contractor shall, at a minimum, perform a follow up oil analysis within a period of two months, maximum, in order to ascertain the extent of any possible problem.
6. Eddy current testing, level 3 for both evaporator and condenser, on 1/3 of chillers each year, to coincide with evaporator cleaning of tube bundles. 7. Open condenser heads, inspect and power brush tubes every season, chemically clean as needed to remove film and coatings that are resistant to abrasive cleaning. Removal of heavy coatings of calcium carbonate associated with improper condenser water treatment or improper control of dissolved solids is outside the requirements of this agreement. Clean 1/3 of the evaporator tubes each beginning with the largest units and proceeding to the smaller units. Additional cleaning to be provided as needed to meet chiller manufacturer’s efficiency ratings. 8. Perform vibration testing on chiller bearing points. Test is to measure vibration amplitude, as a minimum. Provide report of results including analysis of current results and comparison to historical results. B. Semiannual services: 1. Service purge unit and check operation in the following manner: a. Remove and clean condenser, oil separator, and compressor. b. Add new charge of oil-to-oil separator and compressor. c. Recondition purge float valve and reseat as required. d. Lubricate purge motor and inspect belts. e. Install thermocouple in oil separator and set oil heater control. f. Recondition oil separator float valve. g. Leak check purge unit. h. Check for final purge operation and relief valve setting. i. Check purge unit controls and calibrate.
C. Monthly services: General: a. Check all thermometers and gauges on condenser, evaporator and recalibrate or replace. b. Check evaporator, condenser and auxiliary water strainers and clean as required. c. Check refrigerant level; add refrigerant as necessary. d. Check all sight glasses; repair or replace as necessary. 2. Record and Report Results of: a. Running amps and volts. b. Condenser and evaporator pressure drops, water temperature in and out, refrigerant temperature and pressures. c. Check and record oil pressure, temperature level, temperature to bearings, net oil pressure and general condition of oil. d. Comments for correction or adjustment. 3. Provide optimization reports as follows: a. Control strategies implemented. b. Control strategy and other recommendations for correction of deficiencies in plant operation and improvements in efficiency.
SPECIFIC/TECHNICAL REQS - TOTAL SCORES (max 100) |  |  |  | 100